## FRAME_TBL2019Oct
Frame | date_time | Date | inv_status | inv_fault | inv_DC_v | inv_DC_a | AC_out_v | AC_in_v | inv_LED | charger_LED | inv_rev | bat_temp | xformer_temp | FET_temp | inv_model | stack_mode | AC_in_a | AC_out_a | AC_hz | inv_toggle | charger_toggle | eq_toggle | search_w | bat_Ah | bat_type | absorp_v | Charge_a_pct | shore_a | rmt_rev | Parallel_pct | force_charge | gen_auto_start | low_bat_cut_out | AC_in_cut_out_v | float_charge_v | eq_charge_v | absorb_hrs | timeOfDay_hour | timeOfDay_minute | gen_run_hrs1 | gen_start_temp | gen_start_DC_v | quite_time | gen_start_time | gen_stop_time | gen_stop_DC_v | gen_Vstart_delay | gen_Vstop_delay | gen_max_on_hrs | gen_SOC_start | gen_SOC_stop | gen_start_DC_a | gen_Astart_delay | gen_stop_DC_a | gen_Astop_delay | quiet_time_start | quiet_time_end | gen_exercise_days | gen_exercise_start_time | gen_exercise_hrs | top_off_minutes | gen_warm_up_sec | gen_cool_down_sec | bat_eff_pct | resets | bat_size_ah | ags_status | ags_rev | ags_temp | gen_run_hrs2 | ags_bat_v | ags_days_since_run | bmk_soc | bmk_DC_v | bmk_DC_a | bmk_min_v | bmk_max_v | bmk_Ah_in_out | bmk_Ah_trip | bmk_cum_Ah_out | bmk_rev | bmk_fault
1 | 1569931902.8682 | 2019-10-01 | 64 | 0 | 472 | 5 | 118 | 0 | 1 | 0 | 51 | 19 | 36 | 29 | 115 | 0 | 0 | 2 | 600 | 0 | 0 | 0 | 10 | 2180 | 4 | 0 | 100 | 60 | 23 | 60 | 0 | 1 | 420 | 155 | 528 | 12 | 50 | 8 | 11 | 20 | 0 | 440 | 0 | 0 | 0 | 500 | 360 | 600 | 120 | 60 | 90 | 0 | 120 | 20 | 120 | 48 | 24 | 0 | 32 | 10 | 0 | 30 | 30 | 0 | 0 | 600 | 2 | 52 | 252 | 0 | 117 | 1 | 77 | 4730 | -42 | 3908 | 6409 | -137 | 65535 | 183500 | 10 | 1
2 | 1570018300.2596 |  | 64 | 0 | 492 | 6 | 119 | 0 | 1 | 0 | 51 | 21 | 50 | 35 | 115 | 0 | 0 | 2 | 600 | 0 | 0 | 0 | 10 | 2180 | 4 | 0 | 100 | 60 | 23 | 60 | 0 | 1 | 420 | 155 | 528 | 12 | 50 | 8 | 11 | 20 | 0 | 440 | 0 | 0 | 0 | 500 | 360 | 600 | 120 | 60 | 90 | 0 | 120 | 20 | 120 | 48 | 24 | 0 | 32 | 10 | 0 | 30 | 30 | 0 | 0 | 600 | 2 | 52 | 252 | 0 | 121 | 0 | 67 | 4929 | 14 | 3908 | 6409 | -199 | 65535 | 183600 | 10 | 1
3 | 1570041270.8526 | 2019-10-02 | 64 | 0 | 499 | 4 | 120 | 0 | 1 | 0 | 51 | 21 | 60 | 39 | 115 | 0 | 0 | 1 | 600 | 0 | 0 | 0 | 10 | 2180 | 4 | 0 | 100 | 60 | 23 | 60 | 0 | 1 | 420 | 155 | 528 | 12 | 50 | 14 | 34 | 20 | 0 | 440 | 0 | 0 | 0 | 500 | 360 | 600 | 120 | 60 | 90 | 0 | 120 | 20 | 120 | 48 | 24 | 0 | 32 | 10 | 0 | 30 | 30 | 0 | 0 | 600 | 2 | 52 | 252 | 0 | 123 | 0 | 66 | 4981 | 4 | 3908 | 6409 | -206 | 65535 | 183700 | 10 | 1
4 | 1570127669.8594 | 2019-10-03 | 64 | 0 | 508 | 12 | 121 | 0 | 1 | 0 | 51 | 17 | 39 | 28 | 115 | 0 | 0 | 4 | 600 | 0 | 0 | 0 | 10 | 2180 | 4 | 0 | 100 | 60 | 23 | 60 | 0 | 1 | 420 | 155 | 528 | 12 | 50 | 14 | 34 | 20 | 0 | 440 | 0 | 0 | 0 | 500 | 360 | 600 | 120 | 60 | 90 | 0 | 120 | 20 | 120 | 48 | 24 | 0 | 32 | 10 | 0 | 30 | 30 | 0 | 0 | 600 | 2 | 52 | 252 | 0 | 125 | 0 | 70 | 5074 | 32 | 3908 | 6409 | -184 | 65535 | 183800 | 10 | 1
5 | 1570186143.1914 |  | 64 | 0 | 416 | 51 | 122 | 0 | 1 | 0 | 51 | 15 | 44 | 30 | 115 | 0 | 0 | 19 | 600 | 0 | 0 | 0 | 10 | 2180 | 4 | 0 | 100 | 60 | 23 | 60 | 0 | 1 | 420 | 155 | 528 | 12 | 50 | 6 | 48 | 20 | 0 | 440 | 0 | 0 | 0 | 500 | 360 | 600 | 120 | 60 | 90 | 0 | 120 | 20 | 120 | 48 | 24 | 0 | 32 | 10 | 0 | 30 | 30 | 0 | 0 | 600 | 2 | 52 | 252 | 0 | 102 | 0 | 61 | 4154 | -588 | 3908 | 6409 | -241 | 65535 | 183900 | 10 | 1
6 | 1570581360.0002 | 2019-10-08 | 64 | 0 | 440 | 10 | 121 | 0 | 1 | 0 | 51 | 17 | 34 | 24 | 115 | 0 | 0 | 4 | 600 | 0 | 0 | 0 | 5 | 600 | 4 | 0 | 100 | 30 | 23 | 60 | 0 | 0 | 390 | 155 | 528 | 12 | 20 | 0 | 0 | 20 | 0 | 460 | 0 | 0 | 0 | 576 | 120 | 120 | 120 | 0 | 90 | 0 | 120 | 20 | 120 | 80 | 40 | 0 | 32 | 10 | 0 | 60 | 60 | 0 | 0 | 400 | 1 | 52 | 252 | 0 | 108 | 0 | 255 | 4393 | -124 | 4077 | 5011 | 81 | 728 | 0 | 10 | 1
7 | 1570667597.5527 | 2019-10-09 | 64 | 0 | 436 | 9 | 121 | 0 | 1 | 0 | 51 | 17 | 36 | 27 | 115 | 0 | 0 | 3 | 600 | 0 | 0 | 0 | 5 | 600 | 4 | 0 | 100 | 30 | 23 | 60 | 0 | 1 | 380 | 155 | 528 | 12 | 20 | 23 | 57 | 20 | 0 | 396 | 0 | 0 | 0 | 448 | 360 | 480 | 120 | 50 | 90 | 0 | 120 | 20 | 120 | 80 | 40 | 0 | 32 | 10 | 0 | 60 | 60 | 0 | 0 | 400 | 2 | 52 | 252 | 0 | 107 | 0 | 255 | 4356 | -116 | 4077 | 5029 | 71 | 2123 | 200 | 10 | 1
8 | 1570753997.7702 | 2019-10-10 | 64 | 0 | 428 | 8 | 118 | 0 | 1 | 0 | 51 | 15 | 34 | 24 | 115 | 0 | 0 | 3 | 600 | 0 | 0 | 0 | 5 | 600 | 4 | 0 | 100 | 30 | 23 | 60 | 0 | 1 | 380 | 155 | 528 | 12 | 20 | 23 | 57 | 20 | 0 | 396 | 0 | 0 | 0 | 448 | 360 | 480 | 120 | 50 | 90 | 0 | 120 | 20 | 120 | 80 | 40 | 0 | 32 | 10 | 0 | 60 | 60 | 0 | 0 | 400 | 2 | 52 | 252 | 0 | 105 | 1 | 255 | 4281 | -88 | 4077 | 5029 | 2 | 3450 | 300 | 10 | 1
9 | 1570840397.9648 | 2019-10-11 | 64 | 0 | 404 | 14 | 121 | 0 | 1 | 0 | 51 | 14 | 36 | 26 | 115 | 0 | 0 | 5 | 600 | 0 | 0 | 0 | 5 | 600 | 4 | 0 | 100 | 30 | 23 | 60 | 0 | 1 | 380 | 155 | 528 | 12 | 20 | 23 | 57 | 20 | 0 | 396 | 0 | 0 | 0 | 448 | 360 | 480 | 120 | 50 | 90 | 0 | 120 | 20 | 120 | 80 | 40 | 0 | 32 | 10 | 0 | 60 | 60 | 0 | 0 | 400 | 2 | 52 | 252 | 0 | 100 | 0 | 255 | 4052 | -170 | 3729 | 5029 | -89 | 5030 | 500 | 10 | 1
10 | 1570926798.1974 |  | 64 | 0 | 432 | 9 | 120 | 0 | 1 | 0 | 51 | 15 | 54 | 33 | 115 | 0 | 0 | 3 | 600 | 0 | 0 | 0 | 5 | 600 | 4 | 0 | 100 | 30 | 23 | 60 | 0 | 1 | 380 | 155 | 528 | 12 | 20 | 23 | 57 | 20 | 0 | 396 | 0 | 0 | 0 | 448 | 360 | 480 | 120 | 50 | 90 | 0 | 120 | 20 | 120 | 80 | 40 | 0 | 32 | 10 | 0 | 60 | 60 | 0 | 0 | 400 | 2 | 52 | 252 | 0 | 106 | 0 | 255 | 4320 | -110 | 3729 | 5029 | -112 | 6316 | 600 | 10 | 1

## Magnum_Variables
Variable | Type | Units | Name | Segment
Inverter status | int | Code | inv_status | inv
Inverter fault | int | Code | inv_fault | inv
DC volts | int | Volts * 10 | inv_DC_v | inv
DC amps | int | Amps | inv_DC_a | inv
AC volts output | int | Volts | AC_out_v | inv
AC volts input | int | Volts | AC_in_v | inv
Inverter LED | int Bool | On/Off | inv_LED | inv
Charger LED | int Bool | On/Off | charger_LED | inv
Inverter Revision | int | Rev * 10 | inv_rev | inv
Battery temp | int | Deg C | bat_temp | inv
Transformer temp | int | Deg C | xformer_temp | inv
FET temp | int | Deg C | FET_temp | inv
Inverter model | int | Code | inv_model | inv
Stack mode | int | Code | stack_mode | inv
AC Input Amps | int | Amps | AC_in_a | inv
AC Output Amps | int | Amps | AC_out_a | inv
AC Hz | int | Hz * 10 | AC_hz | inv
Inverter Toggle | int Bool | Toggle On/Off | inv_toggle | rem
Charger Toggle | int Bool | Toggle On/Off | charger_toggle | rem
EQ Toggle | int Bool | Toggle On/Off | eq_toggle | rem
Search watts | int | Watts | search_w | rem
Battery size | int | Ah | bat_Ah | rem
Battery Type | int | Code | bat_type | rem
Absorption | int | Volts * 10 | absorp_v | rem
Charger Amps | int | Percent | Charge_a_pct | rem
AC shore amps | int | Amps | shore_a | rem
Remote revision | int | Rev * 10 | rmt_rev | rem
Parallel threshold | int | Percent | Parallel_pct | rem
Force Charge | int | Code | force_charge | rem
Auto Genstart | int | Code | gen_auto_start | rem
Low Battery Cut Out (LBCO) | int | Volts * 10 for 48v | low_bat_cut_out | rem
VAC cut out voltage | int | VAC non-liniar Code | AC_in_cut_out_v | rem
Float Volts | int | Volts * 10 | float_charge_v | rem
EQ Volts | int | (Volts â absorption) * 10 | eq_charge_v | rem
Absorb Time | int | Hours * 10 | absorb_hrs | rem
Time Hours | int | time of day | timeOfDay_hour | A0
Time Minutes | int | time of day | timeOfDay_minute | A0
Gen run time | int | Hours * 10 | gen_run_hrs1 | A0
Start Temp | int | Deg F | gen_start_temp | A0
Start VDC | int | Volts * 10 | gen_start_DC_v | A0
Quiet time hours | int | Code | quite_time | A0
AGS Start Time | int | 15 min units after midnight | gen_start_time | A1
AGS Stop Time | int | 15 min units after midnight | gen_stop_time | A1
AGS Vdc Stop | int | Volts * 10 | gen_stop_DC_v | A1
AGS V Start Delay | int | seconds | gen_Vstart_delay | A1
AGS V Stop Delay | int | seconds | gen_Vstop_delay | A1
AGS Max Run Time | int | Hours * 10 | gen_max_on_hrs | A1
AGS SOC Start | int | percent | gen_SOC_start | A2
AGS SOC Stop | int | percent | gen_SOC_stop | A2
AGS Amps Start | int | Amps | gen_start_DC_a | A2
AGS Amps Start Delay | int | seconds | gen_Astart_delay | A2
AGS Amps Stop | int | Amps | gen_stop_DC_a | A2
AGS Amps Stop Delay | int | seconds | gen_Astop_delay | A2
AGS Quiet Time begin | int | 15 min units after midnight | quiet_time_start | A3
AGS Quiet Time end | int | 15 min units after midnight | quiet_time_end | A3
AGS Exerise Days | int | Days | gen_exercise_days | A3
AGS Exerise Start Time | int | 15 min units after midnight | gen_exercise_start_time | A3
AGS Exerise Runtime | int | Hours * 10 | gen_exercise_hrs | A3
Top off | int | minutes | top_off_minutes | A3
AGS Warm up | int | seconds | gen_warm_up_sec | A4
AGS Cool down | int | seconds | gen_cool_down_sec | A4
Battery efficiency | int | percent | bat_eff_pct | 80
Resets | int | Code | resets | 80
Battery size | int | Ah | bat_size_ah | 80
AGS Status | int | Code | ags_status | AGS1
Revision | int | Rev * 10 | ags_rev | AGS1
Temperature | int | Deg F | ags_temp | AGS1
Gen Runtime | int | Hours * 10 | gen_run_hrs2 | AGS1
AGS vdc | int | Volts * 10 | ags_bat_v | AGS1
Days since last generator run | int | Days | ags_days_since_run | AGS2
State of Charge | int | percent | bmk_soc | BMK
DC volts | int | Volts * 100 | bmk_DC_v | BMK
DC amps | int | Amps * 10 | bmk_DC_a | BMK
Min Volts | int | Volts * 100 | bmk_min_v | BMK
Max Volts | int | Volts * 100 | bmk_max_v | BMK
AmpH in/out | signed int | Ah | bmk_Ah_in_out | BMK
AmpH Trip | int | Ah * 10 | bmk_Ah_trip | BMK
Cumulative AmpH out of Batter1y | int | Ah | bmk_cum_Ah_out | BMK
BMK Revision | int | Rev * 10 | bmk_rev | BMK
BMK Fault | int | Code | bmk_fault | BMK
RTR Revision | int | Rev * 10 | rtr_rev | RTR

## Lead_Acid_Properties
State | Specific
of Charge | Gravity | 6v | 8v | 12v | 24v | 36v | 42v | 48v
100 | 1.277 | 6.37 | 8.49 | 12.73 | 25.46 | 38.2 | 44.565 | 50.93
90 | 1.258 | 6.31 | 8.41 | 12.62 | 25.24 | 37.85 | 44.16 | 50.47
80 | 1.238 | 6.25 | 8.33 | 12.5 | 25 | 37.49 | 43.74 | 49.99
70 | 1.217 | 6.19 | 8.25 | 12.37 | 24.74 | 37.12 | 43.305 | 49.49
60 | 1.195 | 6.12 | 8.16 | 12.27 | 24.48 | 36.72 | 42.84 | 48.96
50 | 1.172 | 6.02 | 8.07 | 12.1 | 24.2 | 36.31 | 42.36 | 48.41
40 | 1.148 | 5.98 | 7.97 | 11.89 | 23.92 | 35.87 | 41.85 | 47.83
30 | 1.124 | 5.91 | 7.88 | 11.81 | 23.63 | 35.44 | 41.35 | 47.26
20 | 1.098 | 5.83 | 7.77 | 11.66 | 23.32 | 34.97 | 40.8 | 46.63
10 | 1.073 | 5.75 | 7.67 | 11.51 | 23.02 | 34.52 | 40.275 | 46.03
from http://www.trojanbattery.com/tech-support/battery-maintenance/
TABLE 1